## flash
Flash Steam Savings Analysis
Part I: | Determining the amount of flash steam produced
A. | Condensate Load |  | 1000 | lbs/hr
B. | Annual hours of operation |  | 3470 | hours
C. | Steam Cost |  | 5 | /1000 lbs produced
D. | Flash Steam percentage from chart below |  | 7%
E. | Flash steam produced: |  | 70 | lbs/hr
D x A = Flash steam produced
Part II: | Determining the Dollar Value of the flash steam
F. | Annual potential flash steam savings |  | 1214.5
| Flash Steam Savings = | E x B x C
1000
Note on G17: Assumes 100% recovery of all flash
Note on G10: Enter as decimal Example: 9% flash enter as .09

## condensate
Condensate Savings Analysis
Condensate Load | * | 1000 | lb/hr
Annual Hours of Operation | * | 3470 | hrs.
Total Water Costs
c1. Untreated water and sewage | * | 0.002 | $/gal
c2. Water treatment chemicals | * | 0.003 | $/gal
Total |  | 0.005 | $/gal
Make-up water preheating requirements
d1. Condensate return temperature | * | 160 | F
d2. Make-up water temperature | * | 60 | F
Total |  | 100 | btu/lb
Steam Cost |  | 5 | $/1000lb
Savings in water costs |  | 2080.3357 | $/yr
Savings for preheating make-up water |  | 1735 | $/yr
Cost of steam to run Armstrong Pump Trap |  | 52.05 | $/yr
Total annual savings |  | 3763.2857 | $/yr
Payback period |  | 1.3454 | yrs.
Equipment cost | * | 5063
Alternative Savings: Less than 100% condensate return
| Annual Savings | Payback Period
90% return | 3386.9572 | 1.4949 | yrs.
80% return | 3010.6286 | 1.6817 | yrs.
75% return | 2822.4643 | 1.7938 | yrs.
70% return | 2634.3 | 1.922 | yrs.
60% return | 2257.9714 | 2.2423 | yrs.
50% return | 1881.6429 | 2.6907 | yrs.
40% return | 1505.3143 | 3.3634 | yrs.
30% return | 1128.9857 | 4.4846 | yrs.
25% return | 940.8214 | 5.3815 | yrs.
Note on C20: Does not include labor and materials to complete installation
An * next to a field indicates required information