Water Temperature Control – Groups of Fixtures – Thermostatic – Rada 320-FMC

Category: Water Heater Control – Groups of Fixtures

Type: Thermostatic

Model: Rada 320-FMC

General:

The Thermostatic Mixing Valve (TMV) shall be of chrome-plated DZR brass/polymer construction.  TMV shall be supplied as standard pre-plumbed and pressure-tested, enclosed in a 26” x 30” x 10” stainless steel recessed cabinet with a 2” flange.  Cabinet shall have a polished stainless steel piano-hinged door with keyed cylinder lock.  TMV shall have optional top or bottom NPT inlets and outlet with integral combination inlet check stop/union/strainers, and outlet stop valve and thermometer.  TMV shall be equipped with a maximum temperature limiting and single temperature locking feature.  TMV shall have dual thermostats for increased accuracy and to provide redundancy in case of individual thermostat failure.

Materials of construction and items included shall be:

•	Chrome-plated DZR brass/polymer

•	Cabinet options:

Premium: 14 gauge #4 finish stainless steel

Standard: 18 gauge #4 finish stainless steel

Baked Enamel: 18 gauge white enameled steel

•	Optional top or bottom 3/4” NPT inlets and outlet

•	Integral combination inlet check stop/union/strainers

•	Outlet stop valve and thermometer

•	Dual thermostats

Performance: TMV shall be so designed that all of the internal operating components are enclosed in a one-piece, “sealed for life” replaceable cartridge for ease of service.  TMV shall be capable of controlling mixed water temperatures +/-2ºF at flow rates between 1 and 24 gpm.  TMV shall be capable of delivering a mixed water temperature that is within 5ºF of either inlet supply temperature.  TMV shall be compliant with ASSE Standard 1017 and CSA B125 and shall be so certified and identified.

The Thermostatic Mixing Valve shall include all of the following capabilities:

•	Maintains mixed water temperatures +/-2ºF at flow rates between 1 and 24 gpm

•	Delivers mixed water temperature within 5ºF of either inlet supply temperature

•	Operational pressure of 10 - 150 psig

•	Thermal shutdown mode upon inlet supply failure