Product: AFH-4400 Stainless Steel Centrifugal Pump and Receiver

Category: Centrifugal Pump and Receiver

Type: Electric

Model: AFH-4400 Stainless Steel

Part 1	General

  - Summary

  - Submittals

  - Delivery, storage and handling

  - Warranty

Part 2	Products

  - Electric Driven Condensate Pump

Part 3	Execution

3.01 Installation

Part 1 – General

  - Summary

- Selection Includes

  - Electric Driven Condensate Pump

  - Submittals

- Submit the following in accordance with this specification:

  - Tag number as referred to on drawing

  - Manufacturer’s name and model number

  - Capacity and Maximum Pressure Ratings

  - Materials of construction

  - Dimensions and weights

  - All other essential data as identified in Owner’s specifications.

  - Delivery, Storage and Handling

- Receipt. Contractor or end user shall receive and store Electric Pump in a manner that will protect them from weather and construction activity.

- Examination. Upon receipt, contractor or end user shall visually inspect all condensate pumps for damage and compare each pump to their corresponding specification.

  - Warranty. Guarantee that the equipment will be free from defects in materials and workmanship for a period of 12 months from date of installation but in no event longer than 15 months after shipment from Armstrong’s factory.

Part 2 – Products

  - Electric Driven Condensate Pump

- Acceptable Manufacturers

  - Armstrong Intl, Inc. Model AFH-4400 Stainless Steel Centrifugal Pump Package

- Receiver shall be constructed of 304 stainless steel with a minimum volume as listed on the schedule. Receiver shall carry a 20 year warranty for failure against corrosion. The receiver shall have, as a minimum, one inlet, one vent and one overflow connection.

- The condensate pump shall be centrifugal type vertically flanged mounted to the receiver. Pump shall be closed-coupled and permanently aligned. Pump housing and flange shall be constructed of cast stainless steel and warranted against failure due to corrosion for a period of 5 years from date of shipment. Pump impeller shall be stainless steel and of semi open design. Impeller shall have balance holes and back pump-out vanes to reduce pressure and/or abrasives in the seal area.

- Duplex unit shall have a mechanical alternator.

- Provide control panel with Nema rated starters NEMA rated motor starters, pump circuit breakers, HOA selector switches, pump run indicator lights, control transformer and liquid tight conduit.

- The complete unit shall be factory assembled and tested prior to shipment.

- Provide tank with stainless steel valve water level gauge with tubular glass sight.

- Provide tank with Bi-metal dial thermometer 2-1/2” face, 4” stem, temperature range from 32°F – 250°F.

- Provide stainless steel suction isolation valve mounted between pump flange and receiver.

Part 3 – Execution:

  - Installation

- Installation Compliance. Install in accordance with manufacturer’s instructions and as shown on the drawing.

End of Section