Steam Series AMAF and AMEF (Series 9000 Area Units) Humidifier

Category: Humidifier

Type: Steam

Model: Series AMAF and AMEF (Series 9000 Area Units)

Steam humidifier for electric control: Humidifier shall be of the steam separator type with full separation ahead of the control valve and with internal drying chamber and steam jacketed outlet to assure discharge of dry steam only.

A. Humidifier shall receive steam at supply pressure.
B. Separating chamber shall be drained by an inverted bucket steam trap.
C. An integral stainless steel steam jacketed solenoid valve shall control flow of steam at supply pressure to the drying chamber. The drying chamber shall be filled with stainless steel silencing material. Vapor shall be discharged from the drying chamber through the steam-jacketed outlet at atmospheric pressure to provide relative humidity at the specified level.
D. A temperature switch shall be employed to prevent humidifier from operating before cold start-up condensate is drained.