Rada Digital Faucet MX1-20NT

Category: Water Temperature Control – Single Point of Use

Type: Digital Faucet

Model: MX1-20NT

- Digital Faucet (MX1-20NT)

  - Digital Faucet shall have non-touch flow (IR) controls

  - Digital Faucet shall have smooth bore laminar flow copper outlet pipe with copper lined insert and flexible PEX lined hoses

  - Digital Faucet shall allow programmable temperatures, flow rates, run time, automated blend duty flush and cold flush, thermal disinfection

  - Digital Faucet shall be of 95% engineering metallics and lead free compliant and IP X4 rated

- MX1-20NT shall have the following operational specifications:

  - +/- 2°F water temperature control

  - Programmable flow rates from 1 – 2.2GPM (3.8 – 8.3LPM)

  - Programmable set point range of 91.4-113°F (33-45°C)

  - Programmable thermal disinfection range of 140-176°F (60-80°C)

  - Automatic safe closure of hot water inlet in response to inlet supply failure, power failure

  - Programmable automatic fixture flush to evacuate stagnant water

  - Operational water pressure range of 14psig (1barg) to 145psig (10barg)

- MX1-20NT shall have the following connectivity specifications:

  - Bluetooth enabled for direct connectivity to the mobile app for field adjustments

  - MODBUS RTU RS485 port for connectivity to either a Local Area Network or integration with a Building Automation System (BAS)

- MX1-20NT shall be certified to ASSE 1070, cUPC, UL1951, UL1310, CAN/CSA C22.2 No. 223, FCC Part 16, NSF 61, NSF 372 (conforms to ASME B112.18.1/CSA B125.1), WaterSense®, DOE Energy Policy Act 1992, ADA, ICC/ANSI A117.1, CSA B651, OBC

- Warranty

  - MX1-20NT shall have a 3-year all mechanical and electrical parts and a 1 year all finish parts warranty