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  Specification


Mechanical Simplex, Cast Iron Electric Condensate Pump Package
Category: Condensate Recovery Equipment
Type: Mechanical
Model: Simplex, Cast Iron Electric Condensate Pump Package
General: Furnish and install according to drawing and manufacturer’s instructions the quantity of single (simplex) condensate pumps(s) as shown on the drawings.  Each unit shall consist of 1 close grained cast iron receiver, 1 water pump , 1 float switch, electric controls and accessories.  Accepted model:  Armstrong FPC Series Simplex Electric Condensate Pumps.

Description:
The condensate receiver shall be manufactured of close grained cast iron.  The receiver shall be equipped with: (1) externally adjustable 2-poled float switch, water level gauge, dial thermometer, (1) pressure gauge for pump discharge,(1) isolation valve between pump and receiver, (2) lifting eye bolts on receivers (25 gal. and larger).

A cast iron “Y” inlet strainer shall be provided for the receiver inlet.

The centrifugal water pump shall be flange mounted on the receiver.  The pump shall be close coupled vertical design, and shall have a cast bronze impeller that is bronze fitted to the cast iron pump housing with a renewable bronze wearing ring.  The pump shall be rated for 200 F condensate.  The entire pump assembly shall be permanently aligned and dynamically balanced to deliver its full rated capacity.  The pump shall be driven by a vertical 3500 RPM open drip proof motor.  The motor shall have a NEMA standard shaft.  The horsepower , and electrical characteristics shall be shown  on the drawings.

Submittals and Testing:
The unit shall be factory tested as a complete unit.  The pump manufacturer shall furnish complete elementary and connection wiring diagrams,  piping diagrams, installation and operation instructions.

Manufacturer’s supplied unit shall be ARMSTRONG  FLUID HANDLING, INC.   221 Armstrong Boulevard, Three Rivers, Michigan 49093

TYPE FPC CONDENSATE PUMPS:
 Model: FPC-1   Simplex
 Capacity: _____________ gpm @ _____________ psig
                   _______________   HP ,       _______________  RPM
 Receiver: _____________ gallons
 Current : _____________  phase, 60 cycles ______ volts
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