Thermostatic TC-C Steam Trap

Category: Steam Trap

Type: Thermostatic

Model: TC-C

Steam trap shall have body clamp to allow for repair of internals. Steam trap shall be balanced pressure type capable of operating close to saturated steam temperature. All wetted parts shall be of 316L grade stainless steel. Body parts shall have internal surface finish of 20 RA or below (equivalent to 180 grit minimum) and external surface finish of 30 RA or below (equivalent to 150 grit minimum). Steam trap shall be completely self-draining when installed in vertical piping. Maximum operating pressure shall be 100 psig.